# COVID-19 Back to Work – Reduction of Virus Spread through Ventilation & Air-Conditioning - Frequently Asked Questions

(Updated 11/03/21)

A good and adequate supply of fresh air ventilation to indoor spaces is part of the university’s wider campus covid-secure risk management strategy to keep everyone safe.

Ventilation is a covid control measure that must be used in a combination with social distancing; the use of hand sanitiser/ hand washing for 20 seconds; the wearing of face coverings at all times (subject to any permitted exemptions); and the periodic cleaning of common touch points.

Since covid restrictions, the university continues to comply with the advice provided by the Health and Safety Executive (HSE) on ‘ventilation and air conditioning during the coronavirus (COVID-19) pandemic’.

These Frequently Asked Questions (FAQ) will summarise the actions taken by the Directorate of Estates and Facilities (E&F) and advice if there is anything that you can do to help.

## FAQ1 - Who provides health and safety guidance in the UK for reducing the risk of the virus spreading through ventilation systems?

The Health and Safety Executive (HSE) sets the strategy, policy and legal framework for health and safety in Great Britain.

The HSE provides ventilation and air conditioning guidance during the coronavirus (COVID-19) pandemic. This is regularly updated as and when new information becomes available.

Within the HSE guidelines, additional guidance from the Chartered Institution of Building Services Engineers (CIBSE) is cited, where the workplace has complex ventilation systems and recirculation units (e.g. air conditioning units, fan coils etc.).

https://www.hse.gov.uk/coronavirus/equipment-and-machinery/air-conditioning-and-ventilation/index.htm

## FAQ2 - How do I know if the ventilation system in my building is safe in preventing the spread of the virus?

University buildings meet Building Regulations requirements for the supply of adequate fresh air.

This can be by natural means such as opening windows or by mechanical systems comprising central ventilation plant, providing ventilation for maximum occupancy in habitable spaces/room.

At this moment in time, with the reduced numbers of staff and students in campus, buildings have adequate or surplus ventilation rates, to that required in the Building Regulations.

## FAQ3 - What practical adjustments have been made to building ventilation and air-conditioning systems to reduce the risk of spread by airborne virus?

During the early stages of the coronavirus (COVID-19) pandemic, the University evaluated building ventilation systems at the whole building/facility level and optimised and adjusted systems so that buildings are ready for reoccupation.

Practical adjustments in line with HSE guidance include:

### Central Ventilation Plant

- Adjusting ventilation recirculation systems, where air taken from a room and conditioned (e.g. heated/cooled/filtered) via central air-handling plant and returned to the room, to operate on full fresh air only.

- Adjusting air heat recovery units (thermal wheels/heat exchangers) to either off or by-pass where appropriate.

- Increasing ventilation plant operating periods by starting earlier and shutting off later by two hours. This will provide purge and flush of the air in spaces they serve.

- Altering ventilation systems based on occupancy levels (e.g. carbon dioxide levels), to maintain higher ventilation levels continuously.

- Adjusting central toilet extract ventilation systems to run continuously

### Local Air-Conditioning Equipment

- Based on current HSE guidance, recirculation units (including air conditioning units), can remain in operation, as long as there is an adequate supply of fresh air and ventilation. Therefore, local air conditioning systems (heat pumps and fan coils units) remain unchanged.

## FAQ4- What can I do to reduce the risk of the airborne virus spread

Good ventilation will help reduce the risk of spreading coronavirus, and in naturally ventilated buildings occupants should;

- Where possible, consider ways to maintain and increase the supply of fresh air, for example, by opening windows and doors (unless fire doors) during occupation.

- In some instances, (e.g. interview rooms, teaching areas etc.) natural ventilation can be further enhanced by airing the space as frequently as possible.                     Where safe to do so, occupants should open vents and windows for 15 minutes prior to and after occupation/use.

## FAQ5 - How will ventilation and air conditioning systems be effected by different strains of the virus

The current advice by the HSE is for the coronavirus (COVID-19) only and for reducing the risk of spread by the supply of adequate fresh air and ventilation. At this moment in time the HSE guidance does not distinguish covid strains or provide alternative control measures for various strains of the coronavirus.

## FAQ6 - How do I raise particular concerns in the space I work?

E&F is working with Faculties and School Safety Managers to ensure actions undertaken are understood, and to communicate any local measures required by occupants, once campus is re-opened i.e. opening windows where possible to increase ventilation, potential thermal comfort issues in the work space, etc.

Any windows opened must be closed properly by the end of the session/working day for security and safety reasons, particularly during inclement weather or high winds.

Where required, Faculty and School Safety Managers will review local risks and concerns outside the control of the E&F, alongside the Government’s coronavirus guidelines.

## FAQ7 - How will the university sustain ventilation safety as scientific advice changes?

E&F will continue to review and take appropriate actions with Faculties and School Safety Managers, as and when new guidance is issued by the HSE.